## Sample 1
A boiler system with two port CV which has a supply of water from pump discharge. Assume constant boiler pressure and 10t/h is produced in boiler and friction losses is constant
[6 empty] | 1 | 2
Answer
Given
Bolier discharge pressure [bar] | 10
Flow[m3/hr] | Pump Discharge pressure [bar] | Delta P [bar] | Kvr [m3/h bar] | Kvr/Kvs % | Reference
0 | 15.58 | 5.58 | 0 | 0% | 1
1 | 15.54 | 5.54 | 0.42486 | 5.272% | 1
2 | 15.42 | 5.42 | 0.85907 | 10.66% | 1
3 | 15.23 | 5.23 | 1.3118 | 16.28% | 1
4 | 14.95 | 4.95 | 1.7979 | 22.31% | 1
5 | 14.58 | 4.58 | 2.3363 | 28.99% | 1
6 | 14.41 | 4.41 | 2.8571 | 35.46% | 1
7 | 13.61 | 3.61 | 3.6842 | 45.72% | 1
8 | 13 | 3 | 4.6188 | 57.32% | 1
9 | 12.31 | 2.31 | 5.9216 | 73.48% | 1
10 | 11.54 | 1.54 | 8.0582 | 100% | 1
As Kvs of 8.06 is not available we move to next one that is 10 and plot the linear and equal percent graph for those
Kvs | 10
Ө | 50
Flow[m3/hr] | Kvr/Kvs % (LINEAR) | Kvr/Kvs % (EQUAL PERCENT) | Reference
0 | 0% | 0% | 2
1 | 4.249% | 19.26% | 2
2 | 8.591% | 37.26% | 2
3 | 13.12% | 48.08% | 2
4 | 17.98% | 56.14% | 2
5 | 23.36% | 62.83% | 2
6 | 28.57% | 67.98% | 2
7 | 36.84% | 74.48% | 2
8 | 46.19% | 80.25% | 2
9 | 59.22% | 86.61% | 2
10 | 80.58% | 94.48% | 2
EP has significantly higher lift to pass same flowrate example for 7m3/hr it has to lift 75%whereas the others 35% and 45%. At low flowrates Ep offers good opening than linear and chances of damage is less to the plug. Here it is water so if linear valve is size perfectly then it is good otherise oversized EP valve is much better option in mos cases
L*100
L𝐼𝑁𝐸𝐴𝑅 %=𝐾𝑣𝑟/𝐾𝑣𝑠*100
𝐾𝑣𝑟=𝑄/√∆𝑃
Q
Q= 𝑒^((𝐻∗ln⁡(𝜃)))/𝜃 "∗Qmax" %𝐻(𝐸𝑃)=100∗(𝑙𝑛 (𝜃∗𝑄)/𝑄𝑚𝑎𝑥)/𝑙𝑛𝜃

## Sample 2
Turbulent Non vapourizing flow sizing
Size a globe valve for a 8inch pipe which has propane flowing through it at 800gpm andd pressure drop across the valve is 25psi. Assume the intial size of valve is 2inch and equal percentage opening
Reference
Given |  |  |  | Legend
Parameter | Value | Units | Reference | Input
Flow rate (q) | 800 | gpm |  | Calculated | 1
Pressure diff (ΔP) | 25 | psi |  | Others
Specific gravity (Gf) | 0.5
Diameter of pipe (Din) | 8 | inch
Numerical constant (N1) | 1 |  | 1
Intial size of valve and its properties
Parameter | Value | Units | Reference
Valve Diameter (d) | 2 | inch
Numerical constant (N2) | 890 |  | 1
Calculate Resistance coefficient
Parameter | Value | Units | Reference
Valve flow coefficient (Cv rated) | 59.7 | - | 2
Valve inlet diameter (d) | 2 | inch
Inlet fitting diameter (D1) | 8 | inch
Outlet fitting diameter (D2) | 8 | inch
Pipe geometry factor (Fp) | 0.86712 | - | 3
Bernoulli inlet coeff. (KB1) | 0.99609 | - | 3
Bernoulli outlet coeff. (KB2) | 0.99609 | - | 3
Inlet resistance coeff.(K1) | 0.43945 | - | 3 |  |  | 2
Outlet resistance coeff.(K2) | 0.87891 | - | 3
∑K = K1 + K2 + KB1 - KB2 | 1.3184 | - | 3
Now calculate the required Cv
Parameter | Value | Units | Reference
Valve flow coefficient (Cv req) | 130.4745 | - | 4
Cv(rated) is < Cv required so 2inch is not suited so move to the size close to Cv req
Given
Parameter | Value | Units | Reference
Flow rate (q) | 800 | gpm
Pressure diff (ΔP) | 25 | psi
Specific gravity (Gf) | 0.5
Diameter of pipe (Din) | 8 | inch |  |  |  |  | 3
Numerical constant (N1) | 1
Intial size of valve and its properties
Parameter | Value | Units | Reference
Valve Diameter (d) | 3 | inch
Numerical constant (N2) | 890
Calculate Resistance coefficient
Parameter | Value | Units | Reference
Valve flow coefficient (Cv rated) | 136 | - | 2
Valve inlet diameter (d) | 3 | inch
Inlet fitting diameter (D1) | 8 | inch
Outlet fitting diameter (D2) | 8 | inch
Pipe geometry factor (Fp) | 0.88243 | - | 3
Bernoulli inlet coeff. (KB1) | 0.98022 | - | 3
Bernoulli outlet coeff. (KB2) | 0.98022 | - | 3
Inlet resistance coeff.(K1) | 0.36926 | - | 3 |  |  |  | 4
Outlet resistance coeff.(K2) | 0.73853 | - | 3
∑K = K1 + K2 + KB1 - KB2 | 1.1078 | - | 3
Now calculate the required Cv
Parameter | Value | Units | Reference
Valve flow coefficient (Cv req) | 128.211 | - | 4
Now Cv (rated) > Cv required so the 3inch valve size will fit this pipe to have a pressure drop of 25psi