## Sample
Design of watercooler using DIN standard design table
Reference
Step 1: Gather data
|  |  |  | Legend | 1
1.1 Shell side |  |  |  | Step
Parameter | Value | Units | Reference | Input
Flow rate (m_s) | 50000 | kg/hr |  | Calculated | 2
Inlet Temp (T1) | 65 | C |  | Other
Outlet Temp (T2) | 50 | C
Density (ρ_s) | 983 | kg/m3
Specific heat capacity (c_s) | 1.16 | Wh/kg K
Heat conductivity (λ_s) | 0.654 | W/m K
Kinematic viscosity (ν_s) | 0.47 | mm2/s
Fouling Factor (f1) | 0.0002 | m2 K/W |  |  | 3
1.2 Tube side
Parameter | Value | Units | Reference
Flow rate (m_t) | 36800 | kg/hr
Inlet Temp (t1) | 15 | C
Outlet Temp (t2) | 35.4 | C
Density (ρ_t) | 994 | kg/m3
Specific heat capacity (c_t) | 1.16 | Wh/kg K
Heat conductivity (λ_t) | 0.605 | W/m K
Kinematic viscosity (ν_t) | 0.92 | mm2/s
Fouling Factor (f1) | 0.0002 | m2 K/W
Step 2: Calculate Heat Loads
Parameter | Value | Units | Reference
Shell side Heat load (Q_s) | 870000 | W | 1
Tube side heat load (Q_t) | 870835.2 | W | 1
Step 3: Determine corrected effective temperature(CMTD)
4
Parameter | Value | Units | Reference
LMTD | 32.2246 | C | 2
P | 0.408 |  | 3
R | 0.73529 |  | 3
F | 0.95 |  | 3
CMTD | 30.6134 | C | 2
Step 4: Estimate the required heat exchanger area
Parameter | Value | Units | Reference
Heat transfer coefficient (U) | 716 | W/m2 K
Area (A) | 39.6912 | m2
Step 5: Selection of appropriate heat exchanger from design table
Parameter | Value | Units | Reference
Shell volumetric flow | 50.8647
Tube volumetric flow | 37.0221 |  |  |  | 5
Based on flow rate we check the table for suitable design which is number 10 heat exchanger design. From DIN Heat exchanger design tables.
6
Parameter | Value | Units | Reference
DN | 500 | mm | 4
N | 164 |  | 4
Vr | 51.12 | m3/hr | 4
Vm | 43.56 | m3/hr | 4
Tube outer diameter | 25 | mm
Tube thickness | 2 | mm
Traingular pitch | 32 | mm
Tube length | 2.5 | m
Area | 12.9 | m2/m
7
Step 6: Determine flow velocity
Parameter | Value | Units | Reference
velocity in tube (w_t) | 0.72422 | m/s | 5
velocity in shell (w_s) | 1.1677 | m/s | 5
Step 7: Determine the convective heat transfer coeff
Shell side heat transfer coefficient
Parameter | Value | Units | Reference
Shell reynolds number (Re_s) | 62111.321 |  | 6
prandtl number (Pr_s) | 2.9501 |  | 6
Nusselt number (N_s) | 167.5222 |  | 6
Heat transfer coefficient (α_s) | 4382.3802 | W/m2 K | 6
Tube side heat transfer coefficient
Parameter | Value | Units | Reference
reynolds number (Re_t) | 16531.1116 |  | 6
prandtl number (Pr_t) | 6.3122 |  | 6
Nusselt number (N_t) | 100.0988 |  | 6
Heat transfer coefficient (α_t) | 2883.7974 | W/m2 K | 6
Step 8: Determine the overall heat transfer coeff
Parameter | Value | Units | Reference
Overall heat transfer coefficient (U) | 985.2688 | W/m2 K
Step 9: Calculate the actual heat load and compare
Parameter | Value | Units | Reference
the total area of heat exchanger | 32.25 | m2
actual heat load Q_actual | 972738.1172 | W
Required overall heat transfer coeff (U_req) | 881.2072 | W/m2 K
Step 10: Calculate the excess and fouling reserve
Parameter | Value | Units | Reference
%reserve | 11.809 |  | 7
With the excess percent being around 12 percent the current heat exchanger design values can be used for obtaining other values and filling up the datasheet.
𝑄=𝑚∗𝑐∗(𝑇1−𝑇2)
𝐿𝑀𝑇𝐷= ((𝑇2−𝑡1)−(𝑇1−𝑡2))/(𝑙𝑛 (𝑇2−𝑡1)/(𝑇1−𝑡2))
𝐶𝑀𝑇𝐷=𝐹 ∗𝐿𝑀𝑇𝐷
𝑤_𝑡= (𝑉_𝑡)/(𝑉_𝑟)∗1
𝑅𝑒= (𝑤∗𝑑)/𝜗
Pr⁡〖= (𝜗∗𝑐∗𝜌∗3600)/𝜆〗
𝑁𝑢_𝑡=0,023∗𝑅𝑒^0,8∗Pr⁡^0.33
𝑁𝑢_𝑠=0,156∗𝑅𝑒^0.6∗Pr⁡^0.33
𝛼=(𝑁𝑢∗𝜆)/𝑑
%𝑟𝑒𝑠𝑒𝑟𝑣𝑒=(𝑈/(𝑈_𝑟𝑒𝑞)∗100)−100