## Problem statement 1
This is a sample pump sizing case study based on an industrial project.

## Solution for 1
Step 1: Gather information
1.1 Physical properties and other constants | [11 empty] | Pictures
Parameter | Value | Units | Reference |  |  | Legend |  |  | Notes | [5 empty] | [3]
Fluid | Water | [-] |  |  |  | User Input |  |  | [1] Engineering Toolbox Database
Temperature | 15 | [C] |  |  |  | Output (calculated from other cells) |  |  | [2] Based on data from question |  |  | [4]
Density | 998.21 | [kg/m3] | (1) |  |  | Text(references, units…etc) |  |  | [3] Crane Handbook (see picture)
Viscosity | 0.0011373 | [Pa s] | (1) |  |  | Result |  |  | [4] see pictures
Specific Gravity | 0.99823 | [-] | (1) | [5 empty] | [5] from manufacturer (see picture)
Vapor pressure | 1705 | [Pa] | (1) | [5 empty] | [6] see picture
Gravity | 9.81 | [m/s2] | [6 empty] | [7] from manufacturer (see picture)
1.2 Operating conditions and operating envelope
Parameter | Value | Units | Notes
Flowrate | 2.6 | [m3/hr]
Point 1
Parameter | Value | Units | Notes
Z1 | 0.25 | [m] | (2)
P1 | 131325 | [Pa]abs | (2)
D1 | 0.2032 | [m] | (2)
A1 | 0.032429 | [m2]
v1 | 0.022271 | [m/s]
Point 2
Parameter | Value | Units | Notes
Z2 | 1 | [m] | (2)
P2 | 131325 | [Pa]abs | (2)
D2 | 0.00635 | [m] | (2)
A2 | 3.1669e-05 | [m2]
v2 | 22.8052 | [m/s]
Step 2: Model Hydraulic Resitances(calculating resistance coefficient and friction headloss for each fitting , component and valve)
2.1 Resistance coefficient table: identification of resistances and equations | [12 empty] | [5]
Parameter | Type | Description | Resistance Coef. Equation |  | Friction Factor equation | Reference | [7 empty] | [7]
K1 | Suction piping | SS 316 pipe sch 10, D=0,0278[m], L=1[m] | K = f L/d |  | for turbulent flow, Re>4000, use Colebrook equation or Swamee Jain equation For laminar flow,Re<2000, use Poseulle equation For transitional flow, 2000<Re<4000 Interpolate between laminar and turbulent flow results. | [3]
K2 | Discharge piping | SS 316 pipe sch 10, D=0,0225[m], L=1,9[m] | K = f L/d |  |  | [3]
K3 | Vessel Exit | SS 316 vessel sch 10 sharp exit/pipe entrance | K = 0.5 |  |  | [3]
K4 | Elbow no.1 | SS 316 90deg. Elbow | K = 30f |  |  | [3]
K5 | Tee No.1 | SS 316 Tee, straight run | K = 20f |  |  | [3]
K6 | Tee No.2 | SS 316 Tee, straight run | K = 20f |  |  | [3]
K7 | Elbow No.2 | SS 316 90deg.Elbow | K = 30f |  |  | [3]
K8 | Spray nozzle | SS316 full jet spray nozzle | K = see the calculation |  |  | [4]
2.2 Resistance coefficient table: evaluation and results
Parameter | L: Length [m] | D: Diameter [m] | Ɛ: Roughness [m] | Relative Roughness [-] | v: Velocity [m/s] | Re: Reynolds[-] | Flow Regime | Friction Factor [-] | K value[-] | hL: Frictional Headloss [m] | Reference
K1 | 1 | 0.0278 | 1.5e-05 | 0.00053957 | 1.1898 | 29032.4072 | Turbulent | 0.0251 | 0.90289 | 0.065151
K2 | 1.9 | 0.0225 | 1.5e-05 | 0.00066667 | 1.8164 | 35871.1521 | Turbulent | 0.024476 | 2.0669 | 0.34757
K3 |  | 0.0278 | 1.5e-05 | 0.00053957 | 1.1898 | 29032.4072 | Turbulent | 0.0251 | 0.5 | 0.036079
K4 |  | 0.0278 | 1.5e-05 | 0.00053957 | 1.1898 | 29032.4072 | Turbulent | 0.0251 | 0.75301 | 0.054336
K5 |  | 0.0225 | 1.5e-05 | 0.00066667 | 1.8164 | 35871.1521 | Turbulent | 0.024476 | 0.48952 | 0.08232
K6 |  | 0.0225 | 1.5e-05 | 0.00066667 | 1.8164 | 35871.1521 | Turbulent | 0.024476 | 0.48952 | 0.08232
K7 |  | 0.0225 | 1.5e-05 | 0.00066667 | 1.8164 | 35871.1521 | Turbulent | 0.024476 | 0.73429 | 0.12348
K8 |  | 0.00635 | 1.5e-05 | 0.0023622 | 22.8052 | 127102.5073 | Turbulent | 0.025926 | 0.82857 | 21.9634
[9 empty] | Total frictional Headloss | 22.7546
2.3 Supporting calculations
Parameter | K8
Type | Spray nozzle
Experimental data for spray nozzle from manufacturer
Q: Flowrate [m^3/s] | Pressure drop [Pa] | Reference
0.00021454 | 34473.8 | [5]
0.0002524 | 48263.32 | [5]
0.00029657 | 68947.6 | [5] | [9 empty] | [6]
0.00041015 | 137895.2 | [5]
0.00056159 | 275790.4 | [5]
0.0007761 | 551580.8 | [5]
0.00085816 | 689476 | [5]
0.0010348 | 1034214 | [5]
Step 3: Calculate pump head required and available NPSH
3.1 Calculate pump work required
Parameter | Value | Units | Reference
Pump work required | 50.0121 | [m] | [6]
3,2 Calculate NPSH available
Parameter | Value | Units | Reference
NPSHa | 13.3312 | [m] | [6]
Step 4: Plot system head and NPSHa
4.1 System head vs Flowrate
Flowrate [m3/hr] | System Head [m] | Reference
0.001 | 3.263 | Fill the flowrate and click generate button it automatically gives he system head
0.6 | 3.3183
0.8 | 4.7685
1 | 6.9345
1.2 | 9.8161
1.4 | 13.413
1.6 | 17.7253
1.8 | 22.7526
2 | 28.4951
2.4 | 42.1248
2.6 | 50.0121
4.2 NPSHa vs Flowrate
Flowrate [m3/hr] | NPSHa [m] | Reference
0.001 | 13.4867 | Fill the flowrate and click generate button it automatically gives he NPSHa
0.6 | 13.4758
0.8 | 13.4685
1 | 13.4596
1.2 | 13.4489
1.4 | 13.4368
1.6 | 13.423
1.8 | 13.4077
2 | 13.3908
2.4 | 13.3526
2.6 | 13.3312
Step 5: Plot pump curve and calculate operating point
Pump type(option 1) | Model DB9
Manufacturer | Finish Thompson
5.1 Pump Head vs Flowrate
Flowrate [m3/hr] | Pump Head[m] | Reference
0 | 20.72 | [7]
0.46 | 20.42 | [7]
0.92 | 20.4216 | [7]
1.38 | 20.2692 | [7]
1.84 | 20.1168 | [7]
2.3 | 19.812 | [7]
2.76 | 19.5072 | [7]
3.22 | 19.2024 | [7]
3.68 | 18.8976 | [7]
4.14 | 18.288 | [7]
4.6 | 17.9832 | [7]
6.9 | 13.716 | [7]
9.2 | 8.5344 | [7]
9.89 | 6.7056 | [7]
10.58 | 3.3528 | [7]
5.2 Numerical calculation of operating flowrate and operating head
System Head Quadratic equation coefficients y = a1x^2 +b1x+c1
a1 | b1 | c1 | Reference
8.9439 | -5.274 | 3.2657 | Change the formulae under a1 alone
Pump Head Quadratic equation coefficients y = a2x^2 +b2x+c2
a2 | b2 | c2 | Reference
-0.1629 | 0.17196 | 20.4193 | Change the formulae under a2 alone
Combined coefficients A = a1-a2, B=b1-b2, C=c1-c2
A | 9.1068
B | -5.4459
C | -17.1536
Operating Point (Root of the above quadratic equation )
Parameter | Value | Units | Reference
Operating Flowrate | 1.7036 | [m3/hr] | Root of quadratic equation
Operating Head | 20.2395 | [m]
5.3 NPSHr vs FlowRate
Flowrate [m3/hr] | NPSHr [m] | Reference
0.9085 | 2.4384 | [7]
3.634 | 3.048 | [7]
6.8137 | 3.9624 | [7]
9.085 | 4.8767 | [7]
Size of Pump Head - 20,23 [m] Flowrate - 1,7 [m3/hr] NPSHr is greater than NPSHa
Generate System Head
Generate NPSHa

## Problem 2
Find Pump power for the following pump given the efficiency of pump is 70% and Q is 10gpm
Step 1: Gather information |  |  |  |  | Legend
User Input
1.1 Physical properties and other constants |  |  |  |  | Output (calculated from other cells)
Parameter | Value | Units | Reference |  | Text(references, units…etc)
Fluid | Water | [-] |  |  | Result
Temperature | 25 | [C]
Density | 1000 | [kg/m3]
Viscosity | 0.0011373 | [Pa s]
Gravity | 9.81 | [m/s2]
1.2 Operating conditions and operating envelope
Parameter | Value | Units | Notes
Flowrate | 10 | [gpm]
| 0.00063 | [m3/s]
Point 1
Parameter | Value | Units | Notes
Z1 | 0 | [m]
P1 | 101325 | [Pa]abs
v1 | 0 | [m/s]
Point 2
Parameter | Value | Units | Notes
Z2 | 4 | [m] | [10 empty] | Reference
P2 | 101325 | [Pa]abs
v2 | 0 | [m/s]
Step 2: Model Hydraulic Resitances(calculating resistance coefficient and friction headloss for each fitting , component and valve)
2.1 Resistance coefficient table: identification of resistances and equations
Parameter | Type | Description | Resistance Coef. Equation |  | Friction Factor equation | Reference | [5 empty] | 1
K1 | Suction piping | 2inch pipe, D=0,0538[m], L=20[m] | K = f L/d |  | for turbulent flow, Re>5000, use Chen equation For laminar flow,Re<2000, use Poseulle equation
K2 | Discharge piping | 3inch pipe, D=0,0780[m], L=8[m] | K = f L/d
K3 | Suction inlet | sharp pipe entrance | K = 0.5
K4 | Discharge outlet | sharp exit | K = 0.5
K5 | Elbow 1 | 2inch pipe, 90deg | K = 30f |  |  | 3
K6 | valve | 3inch | K = 340f |  |  | 3
2.2 Resistance coefficient table: evaluation and results
Parameter | L: Length [m] | D: Diameter [m] | Ɛ: Roughness [m] | Relative Roughness [-] | v: Velocity [m/s] | Re: Reynolds[-] | Flow Regime | Friction Factor [-] | K value[-] | hL: Frictional Headloss [m] | Reference
K1 | 20 | 0.053 | 5e-05 | 0.0009434 | 0.28556 | 13307.6006 | Turbulent | 0.030339 | 11.4486 | 0.047583 | 1
K2 | 8 | 0.078 | 5e-05 | 0.00064103 | 0.13184 | 9042.344 | Turbulent | 0.03267 | 3.3507 | 0.0029687 | 1
K3 |  | 0.053 | 5e-05 | 0.0009434 | 0.28556 | 13307.6006 | Turbulent | 0.030339 | 0.5 | 0.0020781 | 1
K4 |  | 0.078 | 5e-05 | 0.00064103 | 0.13184 | 9042.344 | Turbulent | 0.03267 | 1 | 0.00088598 | 1
K5 |  | 0.053 | 5e-05 | 0.0009434 | 0.28556 | 1e+100 | Turbulent | 0.019352 | 0.58055 | 0.0024129 | 1 |  |  | 3
K6 |  | 0.078 | 5e-05 | 0.00064103 | 0.13184 | 1e+100 | Turbulent | 0.017664 | 6.0057 | 0.0053209 | 1 | 2
[9 empty] | Total frictional Headloss | 0.061249
Step 3: Calculate pump head, pump power
3.1 Calculate pump work required
Parameter | Value | Units | Reference
Pump work required | 4.0612 | [m] | 2
| 39.8409 | [J/Kg]
| 25.0997 | [W]
| 0.033691 | [HP]
Efficiency of pump | 70%
Pump power | 0.04813 | [HP]